SEWAGE PUMPING STATIONS design checklist (CIVIL & MECHANICAL)

The following design checklist is a guide only. The list is not exhaustive and full responsibility for complying with relevant specifications, codes and standards lies with the designer. The checklist shall be completed by the design verifiers and submitted with design drawings.

| SPS No: | Location: | Project No: |  | Delivery Contractor: |  |
| --- | --- | --- | --- | --- | --- |
| Design Stage: | Design Team: |  | Verifiers: |  | Date: |

| ITEM | REQUIREMENTS | YES | NO | N/A | DESCRIPTION |
| --- | --- | --- | --- | --- | --- |
| DRAWINGS AND DESIGN |  |  |  |  |  |
| General | Content is relevant to the scope of work. |  |  |  |  |
|  | All changes to scope documented and agreed. |  |  |  |  |
|  | Sufficient details are shown to enable construction. |  |  |  |  |
|  | Terminology complies with SW Edition of WSA 04, Part 0. |  |  |  |  |
| Orientation | Accurately reflect locality and orientation. |  |  |  |  |
|  | ‘North’ arrows point to the top of drawing sheets (approx.). |  |  |  |  |
| Levels | All Reduced Levels (RL) are in meters and to refer to AHD. |  |  |  |  |
| Dimensions | All dimensions are in millimeters except chainages (in meters). |  |  |  |  |
| Drawing numbering | Comply with SW Asset Plan Numbering System. |  |  |  |  |
| Drawing standard | Comply with SW CAD Standard and Specification. |  |  |  |  |
| Drawing format and title block | Use SW standard drawing templates. |  |  |  |  |
| Labelling | Clearly identify new and existing structures / equipment. |  |  |  |  |
| Services | Show existing and new water, sewage, gas, telecommunication and electricity services. |  |  |  |  |
| Safety in design | SW Safety in Design procedure flowed and documented. |  |  |  |  |
| SITE LAYOUT |  |  |  |  |  |
| Vehicle access, parking and turning | Mobile crane able to reach the wet well, valve chamber, electrical kiosk / switch room, bypass pump connection and insertion points, CDU and OCU (where installed). |  |  |  |  |
|  | Show crane working envelope / radius. |  |  |  |  |
|  | Sufficient setback of gate(s) from main road to enable driver to open / close the gate safely. |  |  |  |  |
|  | Minimum 4m wide access road / driveway. |  |  |  |  |
|  | Minimum four parking spots provided. |  |  |  |  |
|  | Minimum 8m wide x 12m long hardstand area besides the wet well and valve chamber for mobile crane outriggers. |  |  |  |  |
|  | Set down areas for diesel bypass pump(s) and mobile generator provided and labelled. |  |  |  |  |
|  | Turning area suits nominated vehicle type. |  |  |  |  |
|  | Mobile crane (and tanker where CDU provided) able to enter, turn around or drive through and leave the site driving in forward direction. |  |  |  |  |
| Bollards | Concrete footed and filled at access road ends. |  |  |  |  |
|  | Concrete footed and filled if installed along the access road near wet well, valve chamber and structures not designed for vehicular load. |  |  |  |  |
|  | Removable where occasional vehicular access required. |  |  |  |  |
|  | Painted yellow with two strips of red and white reflective tape. |  |  |  |  |
| Site drainage | Shown on drawings. |  |  |  |  |
| Water service | Water service minimum DN100 to site and DN80 within site. |  |  |  |  |
|  | Hydrant(s) DN80 spring type and located close to the wet well and emergency storage. |  |  |  |  |
|  | DN25 hose cock installed on 500mm high galvanised or hardwood post. |  |  |  |  |
| RPZD on water service | Complies with AS2845 and has ‘High Hazard’ PN16 rating. |  |  |  |  |
|  | Main RPZD DN50 and provided with an earthing clamp and conduit. |  |  |  |  |
|  | Additional DN25 RPZDs provided on water supply to CDU and toilet, where applicable. |  |  |  |  |
| External lighting | Shown on site layout drawings. |  |  |  |  |
| Fencing | As per SW DTC drawings. |  |  |  |  |
|  | Type of fence agreed with SW. |  |  |  |  |
|  | Aligned with SW site boundaries (cadastral). |  |  |  |  |
|  | Gate posts installed on the road gutter (not on top of kerb). |  |  |  |  |
| Flood level | 1% AEP level shown on all sectional elevations or note stating that the site is not subject to flooding. |  |  |  |  |
| Landscaping | Low maintenance, as per SW and Local Council’s requirements, if applicable. |  |  |  |  |
|  | Use 40mm gravel (stones). No grass. |  |  |  |  |
|  | Natural shrubs planted on embankments. |  |  |  |  |
| Land and easement acquisition details | Survey coordinates of new acquisition shown on drawings. |  |  |  |  |
| FOUNDATION DESIGN (refer to Technical Specification – Civil, cl. C10) |  |  |  |  |  |
| Geotechnical Investigations | Available geotechnical investigation locations shown on drawings. (eg. boreholes indicated on site plans). |  |  |  |  |
|  | Geotechnical Factual Report Produced |  |  |  |  |
|  | Geotechnical Interpretive Report Produced |  |  |  |  |
| Ground conditions | Bearing capacity and ground (lateral and vertical) movement checks have been carried out and considered in foundation design. |  |  |  |  |
|  | Bearing capacity and ground movement checks documented in Design Report. |  |  |  |  |
|  | Provide values of ultimate bearing capacity and strength reduction factor considered for each structure. |  |  |  |  |
|  | Provide estimated ground movement values as appropriate at each structure (eg. differential settlement between wet well and valve chamber). |  |  |  |  |
|  | Ground condition detail and on-site verification requirements indicated on drawings. |  |  |  |  |
| EARTHWORKS (refer to Technical Specification – Civil, cl. C2 & C10) |  |  |  |  |  |
|  | Required backfill material details specified on drawings, in compliance to Technical Specification – Civil, cl. C2. |  |  |  |  |
|  | Compaction requirements and testing frequency specified on drawings in compliance to SW Technical Specification – Civil, cl. C2. |  |  |  |  |
|  | Selected fill specified for fill material around underground structures and shown on drawings in compliance to Technical Specification – Civil, cl. C2. |  |  |  |  |
| ROADWORKS (refer to Technical Specification – Civil, cl. C8 & C10) |  |  |  |  |  |
| Geotechnical subgrade | Geotechnical subgrade testing carried out and documented in Geotechnical Factual Report. |  |  |  |  |
|  | Provide no. of tests undertaken / available and used for design, documented in Geotechnical Interpretive Report. |  |  |  |  |
|  | Provide minimum and maximum CBR values. Document in Design Report and Specify site verification requirements on drawings. |  |  |  |  |
| Pavements | Pavement designed considering geotechnical subgrade test results. |  |  |  |  |
|  | Provide CBR value adopted for design. |  |  |  |  |
| INLET MH |  |  |  |  |  |
| Top of inlet MH | Slab/roof level min. 300mm higher than 1% AEP level and max. 25mm higher than the surrounding concrete slab or ground. |  |  |  |  |
|  | All perimeter concrete edges chamfered at 25mm x 45O. |  |  |  |  |
| Inlet MH structure | Inside diameter at invert not less than 1800mm excluding any benching. |  |  |  |  |
| Location of Inlet MH | Within SPS site and at sufficient distance from the wet well to allow for a rocker pipe, or otherwise integral part of the wet well. |  |  |  |  |
| Protective coating | Unless agreed otherwise with Sydney Water, all internal concrete surfaces of walls and roof slab coated in accordance with WSA 201. |  |  |  |  |
|  | SW sealing details used at all penetrations. |  |  |  |  |
| Provision for electric bypass pump | Provided min. ø900mm clear path to the invert. |  |  |  |  |
|  | Electrical turret provided next to the inlet MH. |  |  |  |  |
|  | Electrical conduit terminates 100mm behind the edge of access opening and max. 600mm below TOC. |  |  |  |  |
| Connecting pipe to additional emergency storage (where provided) – Low-level fill/drain line | Size equal or larger than the size of the low-level inlet line to the wet well. |  |  |  |  |
|  | IL at inlet MH min. 150mm above the obvert of the low-level inlet line to the wet well. |  |  |  |  |
|  | Inlet MH end of the line flanged. |  |  |  |  |
|  | Min. 150mm clearance between back of the flange and the wall. |  |  |  |  |
|  | Puddle flange provided in all wall penetration. |  |  |  |  |
| Connecting pipe to additional emergency storage (Configurations 2 & 3) – High-level fill line | Size equal or larger than the size of the low-level inlet line to the wet well. |  |  |  |  |
|  | IL at inlet MH min. 150mm above the obvert of the low-level inlet line to the wet well. |  |  |  |  |
|  | Inlet MH end of the line flanged. |  |  |  |  |
|  | Min. 150mm clearance between back of the flange and the wall. |  |  |  |  |
|  | Puddle flange provided in all wall penetration. |  |  |  |  |
|  | The obvert of the high-level fill line at the emergency storage structure min. 100mm and at the inlet MH min. 150mm below the overflow weir crest level. |  |  |  |  |
| Connecting pipe to wet well - Low-level inlet line | Flow capacity at least equal to the flow capacity of the upstream system. |  |  |  |  |
|  | Size equal or larger than the largest inlet line into the inlet MH. |  |  |  |  |
|  | Provision for double isolation of wet well. |  |  |  |  |
| Connecting pipe to wet well - High-level inlet line | Size equal or larger than the size of the low-level inlet line to the wet well. |  |  |  |  |
|  | Inlet MH end of line flanged. |  |  |  |  |
|  | Min. 150mm clearance between back of the flange and the wall. |  |  |  |  |
|  | Puddle flange provided in all wall penetration. |  |  |  |  |
|  | Obvert level of pipe at inlet MH min 150mm below weir crest level and graded towards the wet well. |  |  |  |  |
|  | Offset in relation to the low-level inlet line in the wet well by min. one inlet line diameter/ |  |  |  |  |
| Connecting pipe to emergency relief gas check MH (if emergency relief is off inlet MH) | Obvert of the pipe at the inlet MH min. 300mm below the weir crest level. |  |  |  |  |
|  | Pipe one size greater than the low-level wet well inlet line. |  |  |  |  |
| Scum baffle on emergency relief pipe (if emergency relief is off inlet MH) | Baffle to extend 50 mm below and 150 mm above pipe outlet. Note: if obvert of the connecting pipe is min. 300mm below the weir crest level, then scum baffle in the inlet MH is not required. |  |  |  |  |
| Level sensor | Hydrostatic type. |  |  |  |  |
|  | Shown location and type (positioned slightly above obvert of the wet well low-level inlet line). |  |  |  |  |
| Level switch | Buoyancy type. |  |  |  |  |
|  | Shown location and type (positioned at weir crest level). |  |  |  |  |
| Grit collection | Provided where grit collection is required. |  |  |  |  |
| Personnel access | Stainless steel access ladder or individual stainless steel step irons to AS1657. |  |  |  |  |
|  | Top rung / step iron max. 400mm below TOC. |  |  |  |  |
|  | Ladder rungs / step irons extend min. 150mm into the access opening and positioned at the narrow side of the access opening. |  |  |  |  |
|  | Ladder / step irons landing in IMH maximized. |  |  |  |  |
| Covers | Hinged lightweight (aluminum) with hinged stainless steel safety grilles in non-trafficable areas. |  |  |  |  |
|  | Heavy duty split solid-top type with removable stainless steel safety grille in trafficable areas. Sufficiently sized concrete apron provided in the direction of covers opening on which the covers can be readily placed. |  |  |  |  |
|  | Min. clear opening 1000mm x 1150mm. |  |  |  |  |
|  | Hinged covers positioned and designed such that the cover and safety grille lie flat when fully open. |  |  |  |  |
| Permanent survey label plate | Label plates engraved Gr. 316 stainless steel. |  |  |  |  |
|  | Installed in the concrete surround of the Inlet MH cover. |  |  |  |  |
| WET WELL |  |  |  |  |  |
| Top of wet well | Slab/roof level min. 300mm higher than 1% AEP level and max. 25mm higher than the surrounding concrete slab or ground. |  |  |  |  |
|  | All perimeter concrete edges chamfered at 25mm x 45O. |  |  |  |  |
| Low-level and high-level inlet lines | Metallic (DI or stainless steel) pipes in all wall penetrations. |  |  |  |  |
|  | Puddle flanges provided in all wall penetration. |  |  |  |  |
| Low-level line from emergency storage (Configurations 2 & 3 only) | Metallic (DI or stainless steel) pipes in all wall penetrations. |  |  |  |  |
|  | Puddle flanges provided in all wall penetration. |  |  |  |  |
|  | Size not less than the size of the low-level inlet line. |  |  |  |  |
|  | Wet well end of line fitted with an isolating resilient seated gate valve. |  |  |  |  |
| Inlet isolation valve | Resilient seated gate valve up to DN600 or Gr. 316 stainless steel knife gate valve above DN600. |  |  |  |  |
|  | Provided with Gr. 316 stainless steel extension spindle with stainless steel support brackets. |  |  |  |  |
|  | Standard surface box provided in roof above the inlet valve. |  |  |  |  |
|  | Access opening in the roof provided for valves ≥DN375. |  |  |  |  |
|  | Valve supported inside the wet well on concrete plinth. |  |  |  |  |
|  | No valve gearbox installed in the wet well. |  |  |  |  |
|  | Valves ≥DN450 electrically actuated. |  |  |  |  |
|  | Electric actuator pedestal and enclosure or locking plate details shown. |  |  |  |  |
|  | Actuator pedestal installed on support bracket or adequately strengthened metal cover. |  |  |  |  |
| Low-level inlet | Flanged Gr. 316 stainless steel Sch. 10S drop tube provided for wet wells with two pumps. |  |  |  |  |
|  | Tip of drop tube extends to the pump cut-out level and is cut at 45O. |  |  |  |  |
|  | Baffle wall / plate provided for three or more pumps in wet well as per design guidelines. |  |  |  |  |
| Wet well floor | Provided with min. 1% grade to sump and self-cleansing benching all around. |  |  |  |  |
|  | Provided 1000mm sq. nearly flat (0.5% fall to sump) area directly below personal access hatch for maintenance work box. |  |  |  |  |
| Ventilation arrangement | Natural ventilation via induct and educt vents. |  |  |  |  |
|  | Educt vent line connected to the educt vent shaft. |  |  |  |  |
|  | Induct vent 600mm high Gr. 316 stainless steel box installed close to electrical turrets (min. 300mm apart). |  |  |  |  |
|  | Induct vent positioned so that it does not obstruct laying of access cover flat on ground. |  |  |  |  |
|  | Induct vent line extends to 1m above pump cut-in level (show RL on drawings) and its centerline max. 1000mm away from the low-level inlet line. |  |  |  |  |
|  | Maximised distance between the induct and educt line connections to the wet well (ideally diagonally opposite) to prevent short-circuiting. |  |  |  |  |
| Educt vent line | Min. DN150 or half the size of the low-level inlet line to the wet well (whichever is the larger), but not larger than DN300 unless provided as part of odour control unit. |  |  |  |  |
|  | Length of the educt vent from the wet well and inlet MH to the top of the vent shaft max. 25m, or max. 35m if both increased by one nominal size. |  |  |  |  |
|  | Connected to the wet well as close as possible to top slab. |  |  |  |  |
|  | Connected to the inlet MH and emergency storage (where separate from wet well). |  |  |  |  |
| Discharge (riser) pipes | One spool (closing pipe) identified as 'cut on site to suit' if Gr. 316 stainless steel, or min. 25mm thick packer flange provided if DI. |  |  |  |  |
|  | Minimised number of bends. |  |  |  |  |
|  | Min. one size smaller than the pressure main, but not less than the pump throughlet. |  |  |  |  |
|  | Supports every 6m (show detail of wall attachment). |  |  |  |  |
|  | 3mm thick neoprene between supports and discharge pipes. |  |  |  |  |
| Discharge pipework in existing stations | Identify and provide a note to state 'Make good existing pipework'. |  |  |  |  |
|  | Notes detail painting requirements. |  |  |  |  |
| Sump | Located between pumps. |  |  |  |  |
|  | Size 400mm x 400mm x 300mm deep. |  |  |  |  |
| Access covers | Show all covers (typically five for a 2-pump SPS: - one for personnel access, - one for electrical instruments, - one for each pump, and - one for radar level sensor). |  |  |  |  |
|  | Additional cover provided for inlet valve if ≥DN375. |  |  |  |  |
|  | All covers hinged lightweight (aluminum) fitted with hinged stainless steel safety grilles. |  |  |  |  |
|  | Min. clear opening sizes: - personnel access: 1000mm x 1000mm - electrical instruments: 450mm x 450mm - pumps: min. 75mm clearance all around pump - radar level sensor: 200mm x 300mm - inlet valve: min. 75mm clearance all around valve |  |  |  |  |
|  | Show the mass of each cover and its unobstructed operation. |  |  |  |  |
|  | Where referring to standard SPS DTC drawings, sufficient dimensions provided to enable fabrication of frames and covers. |  |  |  |  |
|  | Hinged covers designed and positioned such that the covers and safety grilles lie flat when fully open. |  |  |  |  |
|  | Hooks for cables aligned with their conduits. |  |  |  |  |
|  | Hooks for pump lifting chains positioned on opposite side to the hooks for cables. |  |  |  |  |
| Personnel access | Show ladder tie points, safety harness anchor points etc. |  |  |  |  |
| Location of pumps in relation to access openings | Dimensions shown on drawings. |  |  |  |  |
|  | Openings aligned with the pumps and provide adequate clearance when flush valves are fixed to the pumps. |  |  |  |  |
| Guide rails | Gr. 316 stainless steel. |  |  |  |  |
|  | Show distance from the edge of access opening to the centre of guide rails. |  |  |  |  |
|  | Intermediate guide bar support bracket(s) provided every 6m. |  |  |  |  |
|  | 3mm thick neoprene between guide bar support bracket(s) and discharge pipes. |  |  |  |  |
| Level switch | Buoyancy type. |  |  |  |  |
|  | Show location (positioned at ATWL) and type on electrical drawings. |  |  |  |  |
| Level sensors | Radar type. |  |  |  |  |
|  | Hydrostatic (located in a stilling tube) if radar cannot be used. |  |  |  |  |
|  | Show location and type - details shown on electrical drawings. |  |  |  |  |
| Operating levels | Show all operating levels, weir crest level and 1% AEP. |  |  |  |  |
|  | Flushing volume for pressure main HDD section(s) provided below ATWL. |  |  |  |  |
| Protective coating | Unless agreed otherwise by Sydney Water, all internal concrete surfaces of walls and roof slab coated as per WSA 201. |  |  |  |  |
|  | SW sealing details used at all penetrations. |  |  |  |  |
|  | Not required at floor of the wet well. |  |  |  |  |
|  | Coating terminating end self-draining. |  |  |  |  |
| Permanent survey mark and survey label plate | Located on wet well roof slab near the el. instruments hatch. |  |  |  |  |
|  | Survey mark in brass. |  |  |  |  |
|  | Label plates engraved Gr. 316 stainless steel. |  |  |  |  |
| EMERGENCY RELIEF SYSTEM |  |  |  |  |  |
| Top of gas check structure | Slab/roof level min. 300mm higher than 1% AEP level and max. 25mm higher than the surrounding concrete slab or ground. |  |  |  |  |
|  | All perimeter concrete edges chamfered at 25mm x 45O. |  |  |  |  |
| Gas check MH structure | Diameter at invert min. 1800mm. |  |  |  |  |
| Location of gas check MH | Preferably within SPS site and at sufficient distance from the inlet MH to allow for a rocker pipe, or otherwise integral part of the inlet MH. |  |  |  |  |
| Personnel access | Stainless steel access ladder or individual stainless steel step irons to AS1657. |  |  |  |  |
|  | Top rung / step iron max. 400mm below TOC. |  |  |  |  |
|  | Ladder rungs / step irons extend min. 150mm into the access opening. |  |  |  |  |
|  | Provide hand grips / stanchions, 32NB GMS, 1000mm high at 575mm centre, painted bright yellow or retractable hand grips in accordance with AS 1657. |  |  |  |  |
| Covers | Hinged lightweight (aluminum) with stainless steel safety grille in non-trafficable areas. |  |  |  |  |
|  | Heavy duty split solid-top type with removable stainless steel safety grille in trafficable areas. Sufficiently sized concrete apron provided in the direction of covers opening on which the covers can be readily placed. |  |  |  |  |
|  | Min. clear opening 1000mm x 1000mm. |  |  |  |  |
|  | Hinged covers designed and positioned such that the covers and safety grilles lie flat when fully open. |  |  |  |  |
| Overflow pipe and gas check valve | Have min. 0.5% incline from the inlet MH to the gas check MH. |  |  |  |  |
|  | Gas check valve able to fully open freely. |  |  |  |  |
| Emergency relief outlet structure | Concrete headwall with Gr. 316 stainless steel screen. |  |  |  |  |
|  | Energy dissipation downstream and soil stabilization around the structure. |  |  |  |  |
|  | Vehicular access to outlet structure for maintenance. |  |  |  |  |
| EMERGENCY STORAGE |  |  |  |  |  |
| Top of emergency storage structure | Access openings min. 300mm higher than 1% AEP level and max. 25mm higher than the surrounding concrete slab or ground level. |  |  |  |  |
|  | All perimeter concrete edges chamfered at 25mm x 45O. |  |  |  |  |
| Capacity | Confirm emergency storage capacity meets the requirements of Needs Specification |  |  |  |  |
| Access covers | Provide minimum two (more for large footprints) with 1000mm x1000mm clear opening. |  |  |  |  |
|  | Hinged lightweight (aluminium) with hinged stainless steel safety grilles in non-trafficable areas. |  |  |  |  |
|  | Heavy duty split solid-top type with removable stainless steel safety grille in trafficable areas. Sufficiently sized concrete apron provided in the direction of covers opening on which the covers can be readily placed. |  |  |  |  |
|  | A separate min. 450mm x 450mm clear opening for instrumentation provided in trafficable areas. |  |  |  |  |
|  | One of the above access opening located over the deepest part of the storage facility and sized for the required emergency by-pass pump. |  |  |  |  |
| Personnel access | Ladder ties provided adjacent to all access points to secure a portable ladder (fixed ladders shall not be provided). |  |  |  |  |
| Head room inside tank | Minimum 2.2 m. Where space is limited, storage is under road and has small footprint, headroom can be reduced if additional access openings provided. |  |  |  |  |
| Wash-down capability | Storage can be hosed down without entering it. |  |  |  |  |
| Floor | Min. 1% grade towards the outlet. |  |  |  |  |
| Ventilation arrangement | Induct and educt vents. |  |  |  |  |
|  | Educt vent connected to the educt vent shaft. |  |  |  |  |
|  | Induct vents 600mm high Gr. 316 stainless steel box. |  |  |  |  |
| Level sensors | Hydrostatic or radar type. |  |  |  |  |
|  | Show location and type - details shown on electrical drawings |  |  |  |  |
| Permanent survey label plate | Located on roof slab near the instruments. |  |  |  |  |
|  | Label plates engraved Gr. 316 stainless steel showing TOC RL. |  |  |  |  |
| PUMPING UNITS |  |  |  |  |  |
| Pump selection | Power rating margin min. 15% over pump operating range from zero flow to 110% of duty flow and non-overloading at minimum head condition. |  |  |  |  |
|  | Motor not to stall at any point on pump performance curve. |  |  |  |  |
|  | NPSHr appropriate under all operating conditions. |  |  |  |  |
|  | Min. 2m NPSH margin under all operating conditions. |  |  |  |  |
|  | Normal duty range between 50% and 120% of BEP flow rate. |  |  |  |  |
|  | Overall efficiency at the nominated duty point min. 40%. |  |  |  |  |
|  | For pumps with VSDs, the impeller diameter selected to meet the duty point at 95% of maximum speed. |  |  |  |  |
|  | For fixed speed pumps, the impeller diameter min. one size smaller than the maximum size that the pump can accommodate. |  |  |  |  |
|  | Pump selected for 50Hz max. speed. |  |  |  |  |
|  | Pumping units comply with WSA 101 and SW Supplement. |  |  |  |  |
| Hydraulic flush valve | Fitted to at least one pump (typically pump no. 1) facing the benching. |  |  |  |  |
|  | Where not feasible, use a return flush line off discharge pipes. |  |  |  |  |
| Pump numbering | From left to right viewed from upstream of the wet well in the direction of flow. |  |  |  |  |
| Pump and motor data | Details shown on drawings in a pump and motor data table. |  |  |  |  |
|  | Details include: make, model, impeller size, duty point(s), motor rating, speed (range), voltage, no. of phases, starter type, overall mass. |  |  |  |  |
| Pump pedestal / discharge connection | Comply with WSA 101 and SW Supplement. |  |  |  |  |
|  | Installed as per SW requirements. |  |  |  |  |
|  | Installation details shown on drawings and described in notes. |  |  |  |  |
| Taper on discharge line | Any tapers next to pump footstep bend eccentric. |  |  |  |  |
| VALVE CHAMBER |  |  |  |  |  |
| Top of valve chamber | Slab/roof level min. 300mm higher than 1% AEP level and max. 25mm higher than the surrounding concrete slab or ground. |  |  |  |  |
|  | All perimeter concrete edges chamfered at 25mm x 45O. |  |  |  |  |
| Location | At sufficient distance from the wet well to allow for a rocker pipe, or otherwise integral part of the wet well. |  |  |  |  |
| Pipework clearances | As per SW Edition of WSA 04 and relevant DTC drawing(s). |  |  |  |  |
| Pipework set-out | Dimensions shown on drawings. |  |  |  |  |
| Pipework and valve materials | All metallic (DI or stainless steel). |  |  |  |  |
| Valve sequence on each pump discharge pipe | In direction of flow: non-return valve, load bearing dismantling joint, then isolating valve. |  |  |  |  |
|  | Air release valves upstream of the non-return valves provided where the depth from the discharge pipe obvert level to the bottom of the wet well is ≥10m. |  |  |  |  |
| Pressure main isolation valve position | Downstream of scour and upstream of bypass connection. |  |  |  |  |
| Isolation valves | All isolation valves resilient seated gate type with non-rising spindle. |  |  |  |  |
|  | All valves ≥DN450 electrically actuated. |  |  |  |  |
|  | If electrically actuated show pedestal and enclosure or locking plate details. |  |  |  |  |
|  | Pedestals installed on top of valve chamber cover. |  |  |  |  |
| Valve extension spindles | Provided with support brackets and finish 50 mm underside of the valve chamber cover. |  |  |  |  |
|  | Provide ø80mm holes above valve spindles. |  |  |  |  |
|  | All openings in gratings cut and banded before galvanizing. |  |  |  |  |
| Non-return valves | All non-return valves long bodied swing check type with extended hinge pin, lever and counterweight and guard. |  |  |  |  |
|  | Counterweight positioned away from normal personnel access path, eg. to face valve chamber walls. |  |  |  |  |
|  | Proximity no-flow (limit) switches installed. |  |  |  |  |
|  | Provide hooks on valve chamber walls to hang levers and counterweights if not used. |  |  |  |  |
| Valve supports | Concrete supports with separating 3mm thick neoprene sheet provided under all valves. |  |  |  |  |
| Air release valves | Fully metallic bodied, suitable for sewage application. |  |  |  |  |
|  | Exhaust piped back to the wet well. |  |  |  |  |
|  | Provide isolating valve upstream of air release valve. |  |  |  |  |
|  | Isolating ball valve provided in exhaust pipe. Valves ≥DN50 of 2-part design with PTFE seals and long handles. Handles to operate in vertical plane (up and down only). |  |  |  |  |
|  | Provide a 3-way union in exhaust pipe near the valve for valve removal. |  |  |  |  |
| Scour line | Scour isolating valve positioned next to branch off tee on the pressure main to reduce solids accumulation. |  |  |  |  |
|  | Drains to the wet well. |  |  |  |  |
| Drain line | Min. DN100 PVC-U or PE pipe. |  |  |  |  |
|  | Outlet fitted with a P-trap and flap valve inside the wet well. |  |  |  |  |
|  | Duck bill valve and a rodding pipe used instead of flap valve where overflow level is higher than the valve chamber floor level. |  |  |  |  |
|  | P-trap and check / duck bill valve installed parallel to wet well wall. |  |  |  |  |
|  | Duck bill valve positioned min. 1m below the valve chamber invert level. |  |  |  |  |
|  | An aluminium surface box with hinged cover provided above the rodding pipe with a label ‘Rodding pipe’ next to it. |  |  |  |  |
|  | Valve chamber graded towards the drain. Benching flush with drain line invert. |  |  |  |  |
| Wet well flushing line (where installed) | Connected upstream of pump discharge non-return valves. |  |  |  |  |
|  | Use electrically actuated eccentric plug valve for control. |  |  |  |  |
| Dismantling joints | All dismantling joints thrust bearing type. |  |  |  |  |
| Puddle flanges | Provided at all wall penetrations. |  |  |  |  |
| Access covers | Open grating galvanized steel. Marine grade aluminium or Gr. 316 stainless steel chequer plate (if close to coastline or in areas accessible to public, such as parks and reserves) in non-trafficable areas. |  |  |  |  |
|  | Hinged over access ladders. |  |  |  |  |
|  | Open grating to have serrated finish on top. |  |  |  |  |
| Personnel access | Permanent inclined rung type access ladders with handgrips to AS1657. |  |  |  |  |
| Pressure tapping points | DN15 tapping point upstream of each non-return valve, one downstream of each pump isolating valve or common manifold (unless buried) and one downstream of the pressure main isolation valve (unless buried). |  |  |  |  |
|  | All pressure tapping points positioned on top of pipe and fitted with Gr. 316 stainless steel block and bleed 2-part stainless steel ball valves. |  |  |  |  |
|  | One DN15 tapping point with a Gr. 316 stainless steel 2-part ball valve provided between the bypass line isolating valves on bottom of the pipe. |  |  |  |  |
| Permanent survey label plate | Label plate engraved Gr.316 stainless steel. |  |  |  |  |
|  | Installed in the concrete wall to show the valve chamber TOC RL. |  |  |  |  |
| BYPASS ARRANGEMENT |  |  |  |  |  |
| By-pass pump connection point | Quick disconnector type coupling with isolating valve and non-return valve within an above ground concrete bund. |  |  |  |  |
|  | Male Kamlock coupling up to DN100 or female Bauer coupling(s) for >DN100. |  |  |  |  |
|  | DN15 tapping point with Gr. 316 stainless steel 2-part ball valve at the base of coupling (outlet facing floor of bund). |  |  |  |  |
|  | Secured dust caps on coupling to prevent unauthorised removal. |  |  |  |  |
|  | Isolating valve on bypass line positioned next to pressure main branch off tee to avoid solids accumulation. |  |  |  |  |
|  | Provide scour to wet well if bypass line longer than 10m. |  |  |  |  |
| Valve supports | Concrete support blocks with 3mm thick separating neoprene sheet provided under all valves. |  |  |  |  |
| Bund | Drains to the inlet MH (provide a P-trap and a flap in inlet MH turned parallel to the wall). |  |  |  |  |
| Security enclosure | Security enclosure provided if determined necessary by site specific risk assessment (eg. unfenced sites). |  |  |  |  |
| PRESSURE MAIN |  |  |  |  |  |
| Material and size | DICL or HDPE, as per Needs Specification. |  |  |  |  |
| Anchor / thrust blocks | Sized for max. test pressure. |  |  |  |  |
| Velocity | Minimum velocity to control slime and solids build-up. |  |  |  |  |
| Rating | Analysis done to verify surge and fatigue (if applicable). |  |  |  |  |
|  | Min. PN16 in trenched installations. Min. PN20 in trenchless (eg. horizontally directionally drilled) sections. |  |  |  |  |
| Scour | Scours provided at all low points. |  |  |  |  |
| Pigging / rodding points | Provide for trenchless (eg. HDD) sections. |  |  |  |  |
|  | To comply with SW standard details. |  |  |  |  |
| Air release valves | Automatic air release valves provided at high point(s). |  |  |  |  |
|  | Fully metallic, suitable for sewage application. |  |  |  |  |
|  | Installed in a chamber(s) and off roads with provision for connecting line flushing. |  |  |  |  |
|  | Resilient seated gate valve installed upstream of air release valve. |  |  |  |  |
|  | Isolating ball valve provided in exhaust pipe. Valves ≥DN50 of a 2-part design with PTFE seals and long handles. Handles to operate in vertical plane (up and down only). |  |  |  |  |
|  | Provide a 3-way union in exhaust pipe near the valve for valve removal. |  |  |  |  |
|  | Ensure sufficient sealing pressure under min. head. |  |  |  |  |
|  | Air release valves connected to odour control unit and / or vent shaft. If close to pumping station, connected to wet well or educt vent shaft. |  |  |  |  |
| Flow meter | Generally required for large SPSs and where SPS is pumping directly to treatment plant. |  |  |  |  |
|  | Ultrasonic clamp-on type. |  |  |  |  |
|  | Installed in chamber as per flowmeter DTC drawings. |  |  |  |  |
| Pressure main discharge maintenance hole | Internally coated in accordance with WSA 201 and vented. |  |  |  |  |
|  | Two MHs downstream of the discharge MH also coated. |  |  |  |  |
|  | Vent shaft at discharge MH have a diameter equal to the diameter of downstream sewer up to a max size of DN300. |  |  |  |  |
| ELECTRICAL EQUIPMENT – GENERAL REQUIREMENTS |  |  |  |  |  |
| Power supply authority’s substation | Installed outside the SPS fenced perimeter. |  |  |  |  |
|  | If the perimeter fence is within the earthing zone of the HV substation the fence earthing shall comply to relevant AS. |  |  |  |  |
| Pits | All pits sized to provide at least 50% spare capacity. |  |  |  |  |
|  | Provided with drainage. Points of discharge shown on drawings. |  |  |  |  |
|  | Provide min. 1200mm x 1200mm x 900mm deep pit in front of the electrical kiosk or switch room. |  |  |  |  |
| Conduits | Layout of all conduits shown on site plan and detailed on electrical and civil drawings. |  |  |  |  |
|  | Conduits installed such that there is at least 50% spare capacity. |  |  |  |  |
|  | Conduits installed with fall away from electrical pits |  |  |  |  |
| Kiosk - position and orientation | Base of kiosk min. 300 mm above 1% AEP level. |  |  |  |  |
|  | Installed on concrete plinth max. 160mm high measured from surrounding concrete apron. |  |  |  |  |
|  | Oriented so that narrow sides face East and West. |  |  |  |  |
|  | Doors to face the wet well. |  |  |  |  |
|  | Provide a shade structure above the kiosk, unless approved otherwise by Sydney Water. |  |  |  |  |
|  | Doors able to open fully. |  |  |  |  |
|  | Provide a concrete apron with min.1500mm clear space in front and 900mm clearance on both sides of kiosk (for MDF and generator connections) and 600mm at the back. |  |  |  |  |
| Electrical switch room | Brick building to SW DTC drawings. |  |  |  |  |
|  | Include toilet facility with water supplied downstream of RPZD |  |  |  |  |
| Electrical turrets | Base of turrets min. 300mm above 1% AEP. |  |  |  |  |
|  | Roughly positioned at ‘9 and 3 o’clock’ central to the pumps when viewed in the direction of flow. |  |  |  |  |
|  | Positioned min. 1700mm from the opening to which conduits run. |  |  |  |  |
|  | Wider side to face wet well or inlet MH, as appropriate. |  |  |  |  |
| Electricity metering panel | Positioned so that no entry is required into confined spaces. |  |  |  |  |
|  | Located outside of electrical kiosk or building (where provided). |  |  |  |  |
| Telecommunications pit | Located within 5m of switchboard. |  |  |  |  |
| Soft starters | Located in switch room if >125kW. |  |  |  |  |
| VSD | Located in kiosk if ≤22 kW and in mechanically ventilated or air-conditioned switch room if >22 kW. |  |  |  |  |
| SPECIFIC SPS REQUIREMENTS |  |  |  |  |  |
| SPSs receiving trade waste | Provide safety shower and eye wash. |  |  |  |  |
|  | Position shower and eye wash in shade where possible. |  |  |  |  |
|  | Incoming water pipes lagged. |  |  |  |  |
| SPSs with a permanent onsite gas/diesel generator or pump | Installed in acoustic enclosure. |  |  |  |  |
|  | Reachable by a mobile crane and fueling tanker. |  |  |  |  |
|  | All details, including concrete plinth shown on the drawings. |  |  |  |  |
|  | Permanent generator sized to start and run all duty pumps and ancillaries. |  |  |  |  |
|  | Permanent bypass pump min. capacity to meet PDWF. |  |  |  |  |
|  | Pump self-primed in max. 180 seconds from cut-in level. |  |  |  |  |
|  | Provided additional discharge non-return valve outside the enclosure with proximity flow switch and conduit to it. |  |  |  |  |
| MISCELLANEOUS |  |  |  |  |  |
| Pressure main(s) and external pipework | Thrust blocks/thrust forces shown on the drawings. |  |  |  |  |
| Materials schedule | Materials and parts listed on the drawings. |  |  |  |  |
|  | Numbers and description match with the drawings. |  |  |  |  |
|  | Mark numbers not duplicated or combined into one (eg. pipe spools). |  |  |  |  |
|  | For pipes that include puddle flanges, show total length, length from puddle flange to each end and whether pipe ends with a flange, socket or spigot. |  |  |  |  |
| Pipe connection details | All specified in notes. |  |  |  |  |
| Fasteners | Flange fasteners Gr. 316 stainless steel with insulating washers and sleeves where required. |  |  |  |  |
| Maintenance holes | Standard drawings in WSA 02 Sewerage Code of Australia referenced as appropriate to diameter and depth of sewer. |  |  |  |  |
| Grouting | Provided under all baseplates, feet and supports when mounted on concrete base or plinth or fastened to concrete walls, ceilings and floors. |  |  |  |  |
|  | Min. 20mm and max. 50mm thick. |  |  |  |  |
|  | Non-shrinking. |  |  |  |  |
| Signage | ’Do Not Drink’ at water tap post. |  |  |  |  |
|  | ‘No Parking - Sydney Water Vehicles Excepted’ outside gates. |  |  |  |  |
|  | Stop signs at access road ends inside gates. |  |  |  |  |
|  | ‘Confined Space’ on access covers. |  |  |  |  |
|  | ‘Two-Person Lift’ on covers and safety grilles where appropriate. |  |  |  |  |
|  | 10km/hr speed limit sign on access road. |  |  |  |  |
|  | Station facility number outside the fence and at public road. |  |  |  |  |
|  | ‘Do Not Trespass’ on outside the fence. |  |  |  |  |
|  | Affix asset (MAXIMO) numbers on concrete next to buried valves, if any (may need to provide small concrete slab next to valve). |  |  |  |  |
| Chemical dosing or Odour Control Unit | As per SW CDU or OCU Standard Specifications. |  |  |  |  |
|  | CDU tanker bund designed as a water retaining structure in accordance with AS3735 |  |  |  |  |
|  | Bund drainage with isolating valve to IMH provided. |  |  |  |  |
|  | Bund drain fitted with a P-trap and flap in the inlet MH turned parallel to the wall. |  |  |  |  |
|  | Chemical dosing line to IMH of a pipe-in-pipe arrangement for double containment purpose. |  |  |  |  |
|  | Provide break in pipe-in-pipe at the entry into the inlet MH. |  |  |  |  |
|  | Dosing pipe to exit outer pipe in IMH and terminate at an angle (approx. 15o from vertical) above benching. |  |  |  |  |
|  | Outer pipe support details shown on drawings. |  |  |  |  |
|  | HAZMAT box provided on a galvanized post inside the access gate. |  |  |  |  |
| Electrical and civil/mechanical drawings | Consistent with each other. |  |  |  |  |

- Document control

- Ownership

BMIS number:	D0001217

| Role | Title |
| --- | --- |
| Group | Engineering and Technical Support |
| Owner | Manager, Engineering |
| Author | Milan Rubcic, Lead Engineer |

- Change history

| Version | Prepared by | Date | Reviewed by | Approved by | Issue date |
| --- | --- | --- | --- | --- | --- |
| 2 | Milan Rubcic | 03/03/2022 | R. Madhok, N. Keong, R. Faure, D. Dineshharan | Norbert Schaeper | 03/03/2022 |
| 1 | Milan Rubcic | 01/03/2019 | R. Madhok, N. Keong | Ken Wiggins | 01/03/2019 |

- Revision details

| Version No. | Clause | Description of revision |
| --- | --- | --- |
| 2 | Whole document | Minor corrections. |
| 1 | First issue | Not applicable. |