## About & How to Use
About the 'Flow Submission' tool
1 | Version 1.1 - March 2025
2 | Sydney Water uses (average daily) hydraulic demand information to (1) undertake network capacity assessments, and (2) determine applicable 'Infrastructure Contributions', for the development.
3 | The purpose of this tool is to simplify, standardise and serve as a record of the proposed development's hydraulic demands as used for purposes noted above.
4 | This tool must be used for all non-residential developments and mixed developments. Use of this tool for residential only developments is encouraged and is therefore, optional.
5 | If your application involves a knock-down and rebuild, you need to provide the total flow rate; otherwise, for modifications, alterations, or extensions to an existing property, only the additional flow rate is required. Check some examples in 'Concept of Additional Demand' sheet.
6 | In this tool, hydraulic demand calculation is based on Sydney Water's - i) 'Non-residential Average Daily Water Use' guide and ii) default wastewater (WW) discharge factors. Residential rates are from our planning guideline.
7 | This tool captures water demand data from the hydraulic consultant when the standard flow rates from 'Non-residential Average Daily Water Use' guide is not available for the specific category of the development e.g. data centre, sporting fields irrigation etc.
8 | If flow rates and/or discharge factors for a development site do not use any of the standard rates or factors, the applicant must justify it in the 'Consultant Report' sheet.
How to use the 'Flow Submission' tool
1 | This tool uses specific colours for different purpose.
2 | Only yellow cells need manual data entry through out this tool.
a | Blue text indicates potable water Purple text indicates recycled water Brown text indicates wastewater
3 | This tool contains the following sheets for specific purposes as outlined below:
a | Summary sheet: The 'Summary' sheet provides the sum of average daily potable water (PW), wastewater (WW) and recycled water (RW) demands from the development. i) WSC needs to fill out the yellow cells ii) Area and number of dwelling inputs are required for determining the "residential Sub-Type" for capacity check purposes only. Enter total number of dwellings for all stages and total areas (lot size) for all stages. The area is the net developable area excluding road, public reserves, etc. iii) The flow rates will be summarised from 'Data Input' sheet iv) Rest of the information is for Sydney Water use only
b | Data Input sheet: i) This is the main data entry sheet for WSC/Developers. ii) This sheet is divided into 2 sections, the top part labelled as 'Data Entry for standard development type' allows automatic data extraction and calculation for residential and non-residential and some special-use developments with standard values from Water Usage Guide and with the default Wastewater Usage Discharge Factors (WUDF). iii) This top part also allows manual entry for non-standard values (PW:RW ratio, WUDF, etc.) if the developments fall under the categories defined in first two columns in this top section. iv) Then the bottom section is labelled (red font) as 'Data Entry for Non-standard development type'. This part needs full manual entry and there is no automated extraction because the development type is unique and does not fall under any standard category. v) The data entry is all numeric in the standard (top) section of this sheet while the data entry is as required by the columns in the non-standard section (bottom) section. vi) Development Type - These are listed in the 1st column as options to choose from. vii) Development Sub-type - These sub-types in the 2nd column change based on "Development Type" from the 1st column. # Residential development type can be used when the application is related to residential development or mixed-use development. For residential development, the determined flow rates will be used for capacity check purpose only, because Infrastructure Contribution charges are calculated from dwelling/lot numbers and area for residential developments. # When residential Development Type is selected in the 1st column, the sub-types will be available to select from the 2nd column. To determine which residential sub-type to select, please use Summary sheet's "Determine residential sub-type" section and enter total number of dwellings for all stages and areas for all stages whether those stages are included in the current case (or application) or not. # Enter the number of dwelling that are related to the application or case in Column D.
viii) The calculation of water and wastewater (standard) flow rates for residential developments is based on Sydney Water edition of Water Supply and Sewerage Codes. ix) The calculation of potable water (standard) flow rates for non-residential developments are from the updated Water Usage Guide and wastewater discharge rates are determined using WUDF multiplied by the sum of potable water and recycled water. x) For the standard development categories that are found in the updated Water Usage Guide (not requiring bespoke calculation), the top section must be used (see screenshot provided). xi) For development categories (from Water Usage Guide) requiring bespoke calculation, the bottom section must be used (see the screenshot provided). xii) For all non-standard development categories (not found in Water Usage Guide), the bottom section must be used (see the screenshot provided).
c | Consultant Report sheet: i) This sheet must be filled out by the WSC/developer, if non-standard entries of hydraulic flow rates are made in 'Data Input' sheet. ii) WSC/developers must use the 'Consultant Report' for calculating non-standard flow rates and provide screenshots of important methodologies, relevant evidence, report pages, etc. on the empty cells below the evidence table. iii) The evidences recorded on this sheet must be uploaded in eDeveloper.
d | Concept of Additional Demand sheet: This sheet gives examples of the type of information expected in this tool.
"Data Input" sheet

## Summary
Development 'Average Daily Demands' - Version 1.1 - March 2025
Click here to review how to complete the document
Date
Case number
[WSC personel] | Completed by (responsible WSC staff)
Development Description
Determine residential sub-type - for mixed development only - for Capacity Checks only
[number of dwellings in all stages]
| [total area in square metres from all stages] |  | Use above value to determine the development sub-type in the "Data Input" sheet for residential development types.
Sydney Water use only
Proposed average daily potable water use
0 | kL residential |  |  |  | Non-standard flow VS standard demand for non-res only
0 | kL non-residential |  |  |  | (excludes non-standard developments):
0 | kL total PW
[6 empty] | Entered |  | Standard
Proposed average daily recycled water use | [5 empty] | PW + RW |  | Demand
0 | kL residential |  |  |  |  | kL/day |  | kL/day
0 | kL non-residential |  |  |  |  | 0 | #DIV/0! | 0
0 | kL total RW
Proposed non-residential flow rates for Infrastructure
Proposed average daily wastewater discharge |  |  |  |  | Contribution purpose:
0 | kL residential
0 | kL non-residential | [6 empty] | Average potable water demand kL/day): | 0
0 | kL total WW | [6 empty] | Average recycled water demand (kL/day): | 0
[8 empty] | Average wastewater discharge (kL/day): | 0
Status of requirements:
Consultant entry required (Yes/No): |  | No
Data Input sheet completed (Yes/No): |  | Yes |  | These values are guide only, please check if the Consultant Report sheet and Data Input sheet are both completed without relying on the formula.
Consultant report completed (Yes/No): |  | N/A
Duplicate entries found (standard & manual)? |  | No |  | PW | RW | WW
|  |  |  | None | None | None | ¬ Rows
Note on J30: Mohammad Hassan: If "Bespoke" text appears in this cell, this means that the user has entered a development category that requires bespoke calculation. Users must use bottom section of "Data Input" sheet for the development categories requiring bespoke calculation.
Note on B40: Mohammad Hassan: This is activated only when Consultant entry is required, otherwise it's N/A.
Note on I44: Mohammad Hassan: Rows where both standard values and consultant entries are found in "Data Input" sheet from column G to M.

## Data Input
Data Entry for standard development type | [13 empty] | SYDNEY WATER USE ONLY
Development data entry | [5 empty] | Standard factor outputs |  |  |  | Consultant (manual) entry |  |  | Compare consultant entry |  |  | Standard factor outputs |  |  |  | Consultant (manual) entry
Select one option | Select one option | Instruction on Key Metrics | Enter Key Metric value | Select one servicing option [PW and/or RW] | Select one WW servicing option | Standard value PW | Standard value RW | Default WUDF | Standard value WW | Entry required (PW) | Entry required (RW) | Entry required (WW) | with Std total PW (Guide only) |  |  | PW | RW | WUDF | WW | PW | RW | WW | Duplicate Finder |  |  | Std PW | Manual [PW=RW] | 5%
Development type | Development Sub-Type | Instruction on Input type for Column D | Values as instructed in Column C | Will this be serviced with Sydney Water's Recycled Water (RW)? | Wastewater discharge factor category | Average PW demand kL/day | Average RW demand kL/day | Wastewater Usage Discharge Factor | Average WW discharge kL/day | Average PW demand kL/day | Average RW demand kL/day | Average WW demand kL/day | Expected value VS Consultant entry | Development TYPE | SHORT | [7 empty] | PW | RW | WW | L/day
[10 empty] | No entry required | No entry required | No entry required | N/A |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | #VALUE!
[10 empty] | No entry required | No entry required | No entry required | N/A |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | #VALUE!
[10 empty] | No entry required | No entry required | No entry required | N/A |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | #VALUE!
[10 empty] | No entry required | No entry required | No entry required | N/A |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | #VALUE!
[10 empty] | No entry required | No entry required | No entry required | N/A |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | #VALUE!
[10 empty] | No entry required | No entry required | No entry required | N/A |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | #VALUE!
[10 empty] | No entry required | No entry required | No entry required | N/A |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | #VALUE!
[10 empty] | No entry required | No entry required | No entry required | N/A |  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | #VALUE!
Data Entry for non-standard development type - all manual entry - if the development type & sub-type are not found in WUG or require bespoke calculation
Select one option | Entry required | Optional Entry | Optional Entry | Select one option | Entry required |  |  |  |  | Entry required (PW) | Entry required (RW) | Calculated WW (No entry required)
Development Type | Development Sub-type (new) eg. Data centre | Define Key metric & its unit [eg. sqm, number of beds, etc.] | Enter key metric value | Will this be serviced with Sydney Water Recycled Water (RW)? | Wastewater discharge factor (eg. 85%, 90%, etc.) | NOT USED |  |  |  | Average PW demand kL/day | Average RW demand kL/day | Average WW demand kL/day | NOT USED
[16 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Number of entries --> | 0 | 0 | 0 |  | 0 | <-- Max | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[9 empty] | Number of entries required --> | 0 | 0 | 0
Development type and sub-type with key metric
Development Type | Development Sub-Type | Key Metric | Metric Unit
Residential | Single dwelling | Dwelling | Each dwelling
Residential | Town House (<30 units/net ha) | Dwelling | Each dwelling
Residential | Multi-unit (30-60 units/net ha) | Dwelling | Each dwelling
Residential | Multi-unit (61-100 units/net ha) | Dwelling | Each dwelling
Residential | Multi-unit (101-140 units/net ha) | Dwelling | Each dwelling
Residential | Multi-unit (>140 units/net ha) | Dwelling | Each dwelling
Commercial | Aged accommodation - full care | Number of beds | Each bed
Commercial | Aged accommodation - self care | Building area | Square metre
Commercial | Childcare | Building area | Square metre
Commercial | Hotel, motel, serviced apartments | Number of rooms | Each room
Commercial | Office | Building area | Square metre
Commercial | Shopping Centre | Building area | Square metre
Commercial | Laundry, dry cleaner | Bespoke calculation required
Commercial | Café, fast food, butcher, deli | Building area | Square metre
Commercial | Retail Units | Building area | Square metre
Commercial | Medical, veterinary | Building area | Square metre
Commercial | Mechanical Repair | Building area | Square metre
Commercial | Car, Boat Sales | Building area | Square metre
Commercial | Carwash | Bespoke calculation required
Commercial | Club | Bespoke calculation required
Industrial | Heavy Process | Bespoke calculation required
Industrial | Chemical Manufacturing | Bespoke calculation required
Industrial | Printing Manufacturing | Bespoke calculation required
Industrial | Beverage Manufacturing | Bespoke calculation required
Industrial | Light Factory Unit | Building area | Square metre
Industrial | Warehousing | Building area | Square metre
Industrial | Transport, Bus Depot | Building area | Square metre
Special_Use | University | Number of students | Each student
Special_Use | School | Number of students | Each student
Special_Use | Hospital | Number of beds | Each bed
Special_Use | Religious assemblies | Building area | Square metre
Special_Use | Government Depot | Building area | Square metre
Special_Use | Community Centre, Library | Building area | Square metre
Special_Use | Sport Fields With Amenities | Bespoke calculation required
Special_Use | Park & Reserves | Bespoke calculation required
Special_Use | Services: police, ambulance, etc. | Building area | Square metre

## Consultant Report
Consultant Report
This sheet must be used when standard PW, WW & RW factors are not available or appropriate as per the 'Data Input' sheet.
Number of Consultant entries in 'Data Input' sheet: |  | 0
Enter calculation basis in the table below for the consultant entries.
You must attach these documents in eDeveloper.
REFERENCE TABLE - Manual data entry by Hydraulic Consultants (or WSCs)
Select Calculation Basis | Enter Title/ Section/ Page | Enter Author/ Consultant name | Enter Qualification | Enter Date of report | Attached in eDeveloper? (Select Yes/No)
Yes
0 | 0 | 0 | 0 | 0 | 1
CALCULATIONS / SCREENSHOTS (from reports, etc.):
Note on B12: Mohammad Hassan: Select from the list only

## Concept of Additional Demand
|  |  |  | Existing state | [10 empty] | Future state |  |  |  |  | Flow Submission Tool entry
|  |  | Shed | [10 empty] | Swimming pool
| Vacant |  |  |  |  | School | [5 empty] | Vacant |  |  |  |  | School
[5 empty] | 2000 students | [10 empty] | 2000 students
|  | ­ |  |  |  |  | ­ | [5 empty] | ­ |  |  |  |  | ­
[8 empty] | Road | [10 empty] | Road
Alteration of a public school to add a 50kL swimming pool
| Vacant |  |  |  |  | Hospital | [5 empty] | Vacant |  |  |  |  | Hospital
[6 empty] | 200 beds | [10 empty] | 300 beds
|  | ­ |  |  |  |  | ­ | [5 empty] | ­ |  |  |  |  | ­
[8 empty] | Road | [10 empty] | Road
Alteration of an existing hospital to increase the capacity to 300 beds
| Vacant |  |  |  |  | Warehouse | [5 empty] | Vacant |  |  |  |  | Hospital
300 beds
|  | ­ |  |  |  |  | ­ | [5 empty] | ­ |  |  |  |  | ­
[8 empty] | Road | [10 empty] | Road
Demolition of an existing warehouse and construct a hospital with 300 beds
| Vacant |  |  |  |  | Hospital |  |  |  |  | Emergency Dept | [5 empty] | Hospital
[6 empty] | 300 beds | [5 empty] | 50 beds |  |  |  |  | 300 beds
|  | ­ |  |  |  |  | ­ | [5 empty] | ­ |  |  |  |  | ­
[8 empty] | Road | [10 empty] | Road
Duplicate scenario for demonstration only
| Vacant |  |  |  |  | Hospital |  |  |  |  | Emergency Dept | [5 empty] | Hospital
[6 empty] | 300 beds | [5 empty] | 50 beds
|  | ­ |  |  |  |  | ­ | [5 empty] | ­ |  |  |  |  | ­
[8 empty] | Road | [10 empty] | Road
Alteration of the existing hospital to add an
emergency department with 50 bed capacity
[22 empty] | Future | Existing | Additional
[21 empty] | Number of Students: | 693 | 572 | 121
[21 empty] | Avg daily drinking water demand: | 2.0097 | 1.6588 | 0.3509
[21 empty] | Avg daily wastewater discharge: | 1.6632 | 1.3728 | 0.2904
Flow rates only for the additional demand must be included in the tool.
In this case, the additional demand will be from the swimming pool only. Entry related to swimming pool is required in the tool.
Do not include total demand for 2000 students and the swimming pool.
Flow rates only for the additional demand must be included in the tool.
In this case, the additional demand will be from the 100 additional beds only. Entry related to 100 beds is required in the tool.
Do not include total demand for 300 beds.
Because the existing warehouse will be completely replaced with a new hospital, total demand is expected in the tool.
Include the flow rates for all 300 beds in the tool.
Flow rates only for the additional demand must be included in the tool.
In this case, the additional demand will be from the Emergency depart only. Entry related to 50 beds is required in the tool.
Do not include total demand.
Additional
demand
Existing
demand
Total
demand
Concept
Total demand = Existing demand + Additional (extra) demand
Additional demand = 350 - 300 = 50 (beds)
The tool entries are based on 50 beds in this case.
Proposed
total demand
SUMMARY: If your case is a knock-down and rebuild one, you'll need to provide the total flow rate. However, if your application is for any of the following two reasons, you only need to provide the additional flow rate only. ~ making modifications or alterations to an existing property without completely demolishing it (eg. adding a swimming pool to an existing hotel, increasing the number of beds in an existing hospital, etc.) ~ adding an extension (eg. adding a separate building to an existing school for special-needs kids on a vacant land within the school boundary, etc.). Check some examples in 'Concept of Additional Demand' sheet.
Example
The tables on the left are real time examples from flow submission.
The proposal is to construct an additional building in the existing school compound.
This will increase the number of students.
How do we find additional demand from these tables?
The table below is used to demonstrate how to get additional flow. This tool entries should only be from the last column of the table below.

## ADWUT (hidden)
AVERAGE DAILY WATER USAGE (ADWU) OF DIFFERENT PROPERTY TYPE
NOTE: Total 36 categories that include 6 Residential sub-types & 9 Bespoke types and 21 other non-residential sub-types
36 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | Wastewater Input
Development Type | Development Sub-Type | Key Metric | Metric Unit | Average PW Demand x (L / Metric Unit / Day) | Entry for calculation | Source | Res or Non-res or Special | WW discharge factor | Dual - PW (L / Metric Unit / Day) | Dual - RW (L / Metric Unit / Day) | WW EP | L/EP | L/dwelling
Residential | Single dwelling | Dwelling | Each dwelling | 750 | Enter number of dwellings (for this application only): | Water System Planning Guideline V1 Sep2014 | Residential | EP based | 500 | 350 | 3.5 | 150 | 525
Residential | Town House (<30 units/net ha) | Dwelling | Each dwelling | 700 | Enter number of dwellings (for this application only): | Water System Planning Guideline V1 Sep2015 | Residential | EP based | 500 | 350 | 3 | 150 | 450
Residential | Multi-unit (30-60 units/net ha) | Dwelling | Each dwelling | 630 | Enter number of dwellings (for this application only): | Water System Planning Guideline V1 Sep2016 | Residential | EP based | 375 | 320 | 2.5 | 150 | 375
Residential | Multi-unit (61-100 units/net ha) | Dwelling | Each dwelling | 530 | Enter number of dwellings (for this application only): | Water System Planning Guideline V1 Sep2017 | Residential | EP based | 375 | 300 | 2.5 | 150 | 375
Residential | Multi-unit (101-140 units/net ha) | Dwelling | Each dwelling | 440 | Enter number of dwellings (for this application only): | Water System Planning Guideline V1 Sep2018 | Residential | EP based | 375 | 250 | 2.5 | 150 | 375
Residential | Multi-unit (>140 units/net ha) | Dwelling | Each dwelling | 420 | Enter number of dwellings (for this application only): | Water System Planning Guideline V1 Sep2019 | Residential | EP based | 375 | 220 | 2.5 | 150 | 375
Commercial | Aged accommodation - full care | Number of beds | Each bed | 220 | Enter number of beds: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Commercial | Aged accommodation - self care | Building footprint | Square metre | 2 | Enter building area in square meters: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Commercial | Childcare | Building footprint | Square metre | 2.5 | Enter building area in square meters: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Commercial | Hotel, motel, serviced apartments | Number of rooms | Each room | 390 | Enter number of rooms: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Commercial | Office | Building footprint | Square metre | 0.4 | Enter building area in square meters: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Commercial | Shopping Centre | Building footprint | Square metre | 2 | Enter building area in square meters: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Commercial | Laundry, dry cleaner |  | Bespoke calculation required | Consultant | Use the bottom section of this sheet. |  | Non-res special | 95% | 66.67% | 33.33%
Commercial | Café, fast food, butcher, deli | Building footprint | Square metre | 2.5 | Enter building area in square meters: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Commercial | Retail Units | Building footprint | Square metre | 1.5 | Enter building area in square meters: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Commercial | Medical, veterinary | Building footprint | Square metre | 1.5 | Enter building area in square meters: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Commercial | Mechanical Repair | Building footprint | Square metre | 0.6 | Enter building area in square meters: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Commercial | Car, Boat Sales | Building footprint | Square metre | 0.6 | Enter building area in square meters: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Commercial | Carwash |  | Bespoke calculation required | Consultant | Use the bottom section of this sheet. |  | Non-res special | 95% | 66.67% | 33.33%
Commercial | Club |  | Bespoke calculation required | Consultant | Use the bottom section of this sheet. |  | Non-res special | 95% | 66.67% | 33.33%
Industrial | Heavy Process |  | Bespoke calculation required | Consultant | Use the bottom section of this sheet. |  | Non-res special | 95% | 66.67% | 33.33%
Industrial | Chemical Manufacturing |  | Bespoke calculation required | Consultant | Use the bottom section of this sheet. |  | Non-res special | 95% | 66.67% | 33.33%
Industrial | Printing Manufacturing |  | Bespoke calculation required | Consultant | Use the bottom section of this sheet. |  | Non-res special | 95% | 66.67% | 33.33%
Industrial | Beverage Manufacturing |  | Bespoke calculation required | Consultant | Use the bottom section of this sheet. |  | Non-res special | 95% | 66.67% | 33.33%
Industrial | Light Factory Unit | Building footprint | Square metre | 0.3 | Enter building area in square meters: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Industrial | Warehousing | Building footprint | Square metre | 0.4 | Enter building area in square meters: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Industrial | Transport, Bus Depot | Building footprint | Square metre | 0.4 | Enter building area in square meters: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Special_Use | University | Number of students | Each student | 12 | Enter number of students: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Special_Use | School | Number of students | Each student | 12 | Enter number of students: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Special_Use | Hospital | Number of beds | Each bed | 300 | Enter number of beds: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Special_Use | Religious assemblies | Building footprint | Square metre | 1 | Enter building area in square meters: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Special_Use | Government Depot | Building footprint | Square metre | 0.4 | Enter building area in square meters: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Special_Use | Community Centre, Library | Building footprint | Square metre | 0.8 | Enter building area in square meters: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%
Special_Use | Sport Fields With Amenities |  | Bespoke calculation required | Consultant | Use the bottom section of this sheet. |  | Non-res special | 95% | 66.67% | 33.33%
Special_Use | Park & Reserves |  | Bespoke calculation required | Consultant | Use the bottom section of this sheet. |  | Non-res special | 95% | 66.67% | 33.33%
Special_Use | Services: police, ambulance, etc. | Building footprint | Square metre | 0.75 | Enter building area in square meters: | Planning consultant | Non-residential | 95% | 66.67% | 33.33%

## Lists (hidden)
Development Type | Residential | Other (manual entry) | Commercial | Industrial | Special_Use | WWdischarge | RW | RW_REF | Calculation Methodology
Residential | Single dwelling |  | Aged accommodation - full care | Heavy Process | University | Standard | No - PW only (Std value) | YES | Code
Commercial | Town House (<30 units/net ha) |  | Aged accommodation - self care | Chemical Manufacturing | School | Other | Yes - PW&RW (Std value) | NO | Standards
Industrial | Multi-unit (30-60 units/net ha) |  | Childcare | Printing Manufacturing | Hospital | WW not required | Other PW only | OTHER | Technical Guides
Special_Use | Multi-unit (61-100 units/net ha) |  | Hotel, motel, serviced apartments | Beverage Manufacturing | Religious assemblies |  | Other PW & RW ratio | OTHER | Hydraulic Report
| Multi-unit (101-140 units/net ha) |  | Office | Light Factory Unit | Government Depot |  | PW&RW not required | NOT_REQ | Other evidence
| Multi-unit (>140 units/net ha) |  | Shopping Centre | Warehousing | Community Centre, Library
|  |  | Laundry, dry cleaner | Transport, Bus Depot | Sport Fields With Amenities |  | Testing:
|  |  | Café, fast food, butcher, deli |  | Park & Reserves |  | WW not required
|  |  | Retail Units |  | Services: police, ambulance, etc.
Medical, veterinary
|  |  | Mechanical Repair |  |  | ROW#
|  |  | Car, Boat Sales |  |  | 14 | YES | These are tables used for G column in "Data Input" sheet. Do NOT change!
|  |  | Carwash |  |  | 15 | Standard
|  |  | Club |  |  | 16 | Other
[6 empty] | 17 | WW not required
18
[6 empty] | 19 | NO
[6 empty] | 20 | Standard
[6 empty] | 21 | Other
[6 empty] | 22 | WW not required
23
[6 empty] | 24 | OTHER
[6 empty] | 25 | Other
[6 empty] | 26 | WW not required
Key Metric | Metric Unit | Entry for calculation |  |  |  | 27
Dwelling | Each dwelling | Enter number of dwellings (for this application only): |  |  |  | 28
Number of beds | Each bed | Enter number of beds: |  |  |  | 29 | NOT_REQ
Building footprint | Square metre | Enter building area in square meters: |  |  |  | 30 | Other
Number of rooms | Each room | Enter number of rooms: |  |  |  | 31 | WW not required
Number of students | Bespoke calculation required | Use the bottom section of this sheet. |  |  |  | 32
| Each student | Enter number of students:
[6 empty] | 34 | TABLE CALL OUT | Cell_Ref
[6 empty] | 35 | BLANK! | E5
[6 empty] | 36 | BLANK! | E6
[6 empty] | 37 | BLANK! | E7
[6 empty] | 38 | BLANK! | E8
[6 empty] | 39 | BLANK! | E9
[6 empty] | 40 | BLANK! | E10
[6 empty] | 41 | BLANK! | E11
[6 empty] | 42 | BLANK! | E12
[6 empty] | 43 | BLANK! | E13
[6 empty] | 44 | BLANK! | E14
[6 empty] | 45 | BLANK! | E15
[6 empty] | 46 | BLANK! | E16
[6 empty] | 47 | BLANK! | E17
[6 empty] | 48 | BLANK! | E18
[6 empty] | 49 | BLANK! | E19
[6 empty] | 50 | BLANK! | E20
Note on B2: Mohammad Hassan: High Rise missing

## DELETE (hidden)
|  |  | 59.52% | 50.79%
| 25.2 |  | 15 | 12.8
40 | 630 | 25.2 | 15 | 12.8
40 | 375 | 15
40 | 320 | 12.8

## Feedback (hidden)
Issue | Date raised | By | Status | Outcome/Action
Tool is for capacity assessments and IC charging purposes. Therefor res and non-res figures are provided. | 2024-05-27 | Nick | Completed | Non-res flows identifiable on summary page.
WW discharge factors | 2024-06-24 | Nick | Completed | Option to select either 'Standard' or 'Other' WW discharge factors. Standards returns input from 'Average Daily Water Use table'. 'Other' requires input from WSC or consultant and basis of calculation
Average Daily Water Use tables currently being updated | 2024-07-25 | Others | Ongoing | To be updated in the ADW table once completed
PW&RW breakdown - adopted 2/3 & 1/3 accordingly | 2024-06-24 | Nick | Completed | As discussed with Ruth H & Richard W
Option is for all asset streams to have a consultant entry, regardless of whether a standard factor output is achieved. The figure to be used for sum data then should always default to the consultant entry, when there is one. | 2024-07-25 | Hassan (Nick support) | Done
Consultant Report entries completed notifier (Summary sheet) | 2024-07-25 | Hassan (Nick support) | Done
Add detail in 'About' Residential only, not required to use this tool |  | Nick | Done
PW res calculation: - (A) Property area / (B) dwellings = (C) Density X factor for kL | 2024-07-25 | Richard & Matt | Done | ADWU table updated to include
WW res discharge calculation | 2024-07-25 | Richard & Matt | Done | Richard W confirmed as per Sydney wide average.
Standard WW discharge factor |  |  | Done | Confirmed 95% as per the latest WUDF is applicable across the board (industrial/commercial). Other factor requires consultant entry.
Standard WW discharge factor with dual water? | 2024-08-29 | Nick | Done | What is the standard WW discharge when dual water? Richard: Same WUDF will be applied to (PW+RW).
Handover questions: 1. J column WUDF 2. N column’s formula reference should be K, not J 3. Does J column need the text for “Consultant Entry”? Because there is no option (column) for Discharge factor entry! 4. L, M, N will replace the values of H, I & K, is that right? There is no further manipulation required on L, M & N. 5. What is required in column D when the Input type (column C) is "Calculate method required"? 6. Can I replace non-residential category of "As required" | 2024-09-02 | Hassan | DONE | RESPONSES: 1. J column WUDF - YES 2. N column’s formula reference should be K, not J - YES 3. Does J column need the text for “Consultant Entry”? Because there is no option (column) for Discharge factor entry! - NO, PUT N/A. 4. L, M, N will replace the values of H, I & K, is that right? There is no further manipulation required on L, M & N. - YES, YOU'RE RIGHT. 5. What is required in column D when the Input type (column C) is "Calculate method required"? - NOTHING, the cell remains blank.
Repair Nick's formula in Data Input sheet to accommodate Special categories that require consultant entry | 2024-09-02 | Hassan | DONE
Consultant Report sheet needs a form for consultants to make entry to demonstrate evidence and they need to select if they have attached the evidence in eDeveloper (Yes/No only). | 2024-09-02 | Hassan | Drafted for review
Summary sheet needs to have an entry for the tallest building | 2024-09-02 | Hassan | Done

## Algorithm (hidden)
IF | Nested-IF | POTABLE WATER |  |  | RECYCLED WATER
Residential |  | TIMES (X) |  |  | TIMES (X)
| Yes - PW&RW (Std value) | Dual - PW (L / Metric Unit / Day) [ADWUT:9] | D5 |  | Dual - RW (L / Metric Unit / Day) [ADWUT:10] | D5
| No - PW only | Average PW Demand (L / Metric Unit / Day) [ADWUT:4] | D5 |  | 0
| Other PW & RW ratio | Consultant entry required |  |  | Consultant entry required
| PW&RW not required | PW not required |  |  | PW not required
Non-Residential
| Yes - PW&RW (Std value) | Average PW Demand (L / Metric Unit / Day) [ADWUT:4] | Dual - PW (L / Metric Unit / Day) [ADWUT:9] | D5 | Average PW Demand (L / Metric Unit / Day) [ADWUT:4] | Dual - PW (L / Metric Unit / Day) [ADWUT:10] | D5
| No - PW only | Average PW Demand (L / Metric Unit / Day) [ADWUT:4] | D5 |  | 0
| Other PW & RW ratio | Consultant entry required |  |  | Consultant entry required
| PW&RW not required | PW not required |  |  | PW not required
Non-res special
COLUMN H5 (PW)
=IFERROR(
SWITCH($O5,"Residential",
SWITCH($E5,
"Yes - PW&RW (Std value)", VLOOKUP($B5,ADWUT!$B$11:$K$999,9,FALSE)*$D5,
"No - PW only (Std value)", VLOOKUP($B5,ADWUT!$B$11:$K$999,4,FALSE)*$D5,
"Other PW & RW ratio", "Consultant entry required",
"Other PW only","Consultant entry required",
"PW not required"),
"Non-residential",
SWITCH($E5,
"Yes - PW&RW (Std value)", VLOOKUP($B5,ADWUT!$B$11:$K$999,4,FALSE)*VLOOKUP($B5,ADWUT!$B$11:$K$999,9,FALSE)*$D5,
"No - PW only (Std value)", VLOOKUP($B5,ADWUT!$B$11:$K$999,4,FALSE)*$D5,
"Other PW & RW ratio", "Consultant entry required",
"Other PW only","Consultant entry required",
"PW&RW not required"),
"Non-res special",
IF($E5="PW&RW not required", "Not required","Consultant entry required")
), "")
------------------
COLUMN I5 (RW)
=IFERROR(
SWITCH($O5,"Residential",
SWITCH($E5,
"Yes - PW&RW (Std value)",VLOOKUP($B5,ADWUT!$B$11:$K$999,10,FALSE)*$D5,
"Other PW & RW ratio","Consultant entry required",
"RW not required"),
"Non-residential",
SWITCH($E5,
"Yes - PW&RW (Std value)",VLOOKUP($B5,ADWUT!$B$11:$K$999,4,FALSE)*VLOOKUP($B5,ADWUT!$B$11:$K$999,10,FALSE)*$D5,
"Other PW & RW ratio","Consultant entry required",
"PW&RW not required"),
"Non-res special",
"Consultant entry required"),
"")
-----------------------------
COLUMN K5 (WW)
=IFERROR(
SWITCH($G5,
"Other", "Consultant entry required",
"WW not required", "WW not required",
"Standard", IF(ISNUMBER(SEARCH("Consultant", H5)),"Consultant entry required", IF(ISNUMBER($I5), ($H5+$I5)*$J5, $H5*$J5))
),"")